## Cover
Core Site Preventive Maintenance Template
<Date>

## Instructions
Instructions
This document is intended to be used as a checklist to perform preventive maintenance at cell sites, each of the following sheets must be completed by the person responsible for performing it. NaaS Operators may add, delete more items if it's required
Revision Control: | Sheet allows to maintain a record of changes made on the document.
Core Equipment ¦ Grounding &Electrical Dist ¦ Core Power System ¦ Air Conditioning & Facility :
1.- Fill the required data.
2.- Follow the instructions as are indicated in "Condition assesment" column.
3.- In case the respective item don't meet the required condition, perform the service as is indicated.
4.- Detail any Spare part or materials if they have been used / installed in the column "Used material"
5.- Once the item meets the required condition mark the check box in "Aproved condition" column.
6.- Detail if additional repairs are required in "Additional Actions" space .
7.- After the maintenance is performed, Technicians and Management must sign the document.

## Revision Control
Revision Control
Version N° | Issue Date | Status | Reasons for Change

## Core Equipment
Core Equipment Maintenance Checklist
Site Name:
Work Order #: |  | Pending Tasks:
Last Intervention Date:
Intervention Date:
Aproved by:
Performed by:
Item | Condition Assesment | Service (If required) | Used Material | Approved Condition
Servers, Routers, Switches and Storage | Check for visual alarms with the LED indicators .-Verify if the backups are working. | .-There are no alarm indicators .-Create Backups Daily | insert used material
Servers, Routers, Switches and Storage | .-Check disk usage. .-Update Control Panel firmware. .-Check application updates. .-Check remote management tools. .-Check server utilization. .-Review user accounts. .-Check system security. | Contact HW and SW provider in case of high server utilization or SW Malfunction. .-Delete logs and s/w versions that are not in use .-Change passwords .-Update the OS as is required. .-Update Management Tools | insert used material
Servers, Routers, Switches and Storage | Visual Inspection | Clean dust using air blower, ensuring enough space to not damage circuits. | insert used material
Servers, Routers, Switches and Storage | Check that unused Ports and fibers have protective caps | Install caps in unused ports and fibers | insert used material
Additional Actions Required :
Engineer's Signature: |  | Management Signature:
Aproved
Aproved
Aproved
Aproved
Aproved
Aproved
Aproved

## Grounding &Electrical Dist
Grounding & Electrical Distribution Maintenance Checklist
Site Name:
Work Order #: |  | Pending Tasks:
Last Intervention Date:
Intervention Date:
Aproved by:
Performed by:
Item | Condition Assesment | Service (If required) | Used Material | Approved Condition
Fuse and Breakers in electric Panels | .-There are no signs of burn-in Fuse and breaker. .-Proper clearances are maintained. .-There are no signs of excessive deterioration or overheating. | .-Install / Replace Fuses, Breakers .-Rearrange cabling clearances where applies. | insert used material
Grounding clamps and cables. | .-Check if Grounding wire don’t show signs of corrosion .-Check if Grounding bars are not burned .-Check Ground Resistance which should be 1 and 5 Ohm. | .-If the grounding wire is not present, put it in place. .-Replace Grounding wires if it’s required | insert used material
Automatic transfer switch | Perform all mechanical operational tests on both the circuit breaker and its operating mechanism; confirm the proper operation of interlocks and mechanisms. | Contact Vendor Provider if there is sign of malfunction. | insert used material
Additional Actions Required :
Engineer's Signature: |  | Management Signature:
Aproved
Aproved
Aproved
Aproved
Aproved
Aproved
Aproved

## Core Power System
Power System Maintenance Checklist
Site Name:
Work Order #: |  | Pending Tasks:
Last Intervention Date:
Intervention Date:
Aproved by:
Performed by:
Item | Condition Assesment | Service (If required) | Used Material | Approved Condition
UPS, PDU | .-Check if system components are clean .-Check if Input, Output and bypass voltage and current values are within designed specifications. | .-Clean boards using air blower, ensuring enough space to not damage circuits. .-Contact UPS Provider if Voltage is not within designated specifications. | insert used material
UPS & Batteriies | .-Check if Power Ports are correctly connected and insolated .-Input, Output and bypass voltage are within designed specifications. .- Batteries do not produce excessive heat and deliver the right voltage .-Check if there's no liquid contamination from batteries and capacitors. | .-Tight loose connections following vendor procedure .-Clean Battery connections following vendor Specifications .-Contact UPS Provider Capacitors shows any leak. | insert used material
UPS Software | Check UPS Firmware | Update Firmware as required. | insert used material
UPS, PDU | .-Inspect UPS/ PDU components .-Conduct thermal scans on electrical connections using a diagnostic tool .-Measure and check the torque of all connections. .-Load-test the battery bank disconnecting the UPS from its power source. .-For flooded-cell batteries, the technician should: .-Inspect terminals for signs of corrosion and accumulation of dirt .-Measure and record the voltage and current of the entire bank .-Measure and record the voltage for each individual cell and test their electrolytes .-Record and log measurements to track battery performance | .-Re-torqueing any power connections as needed .-Clean signs of corrosions .-Replace batteries if it is required | insert used material
Additional Actions Required :
UPS Battery expiration date:
Engineer's Signature: |  | Management Signature:
Aproved
Aproved
Aproved
Aproved

## Air Conditioning & Facility
Air Conditioning & Facilities Maintenance Checklist
Site Name:
Work Order #: |  | Pending Tasks:
Last Intervention Date:
Intervention Date:
Aproved by:
Performed by:
Item | Condition Assessment | Service (If required) | Used Material | Approved Condition
Core site environment | .–Check room temperature. It must be within 18° C to 27° C .–Check the Relative humidity. It must be less than 60% .–Dew point within the range of 5.5° C to 15° C | Adjust and calibrate Air conditioner and climate controls | insert used material
Air conditioner | .-Check that there are no loud sound and broken hardware .-Check if filters are clean. .-Check if paint is in good condition .-Check if There is no sign of corrosion .-Check that Coil Fins and blades have no damage .-Check that there are no water leaks .-Check if Refrigerant or water levels are within the operative levels. .-Check that there is no excessive amount of water and there is no presence of rust. .-Check ifFan operates normally | .-Replace drive belts, lubricate bearings .-Clean or replace the factory-installed air filter and water filter media. .-Clean or replace the humidifier cylinder. Inspect humidifier water valves. .-Tight electrical connections within the unit. .-Tighten pipe clamps, piping joints, and compressor mounting hardware within the unit. .-Adjust fan speed regulation and controls. .-Repair Leaks as provider maintenance recommendation. .-Fill water supply provider maintenance recommendation. | insert used material
Lights | Check whether the routine and emergency illumination in the equipment room is normal. | Look if fuse or light breakers are switched on, change fuses or ligts if its required. | insert used material
Emergency equipment | .-The foam extinguisher or dry powder fire extinguisher is installed in the equipment room. The pressure and validity period of the extinguisher meets the requirements .-There is no danger of damage to the equipment by rats or insects. | Replace or fill the extinguisher | insert used material
Overall Cleanliness | Check whether cabinets, equipment housing, equipment interior, tables, floor, doors, and windows are clean | Clean the Core site Interior,. looking for possible leaks. | insert used material
Additional Actions Required :
Engineer's Signature: |  | Management Sign:
Aproved
Aproved
Aproved
Aproved
Aproved