## Cover
Cell Site Preventive Maintenance Template
<Date>

## Instructions
Instructions
This document is intended to be used as a checklist to perform preventive maintenance at cell sites, each of the following sheets must be completed by the person responsible for performing it. NaaS Operators may add, delete more items if it's required
Revision Control | Sheet allows to maintain a record of changes made on the document.
Facilities & Shelter ¦ Power System ¦ Baseband & Transmission ¦ Antenna System
1.- Fill the required data.
2.- Follow the instructions as are indicated in "Condition assesment" column.
3.- In case the respective item don't meet the required condition, perform the service as is indicated.
4.- Detail any Spare part or materials if they have been used / installed in the column "Used material"
5.- Once the item meets the required condition mark the check box in "Aproved condition" column.
6.- Detail if additional repairs are required in "Additional Actions" space .
7.- After the maintenance is performed, Technicians and Management must sign the document.

## Revision Control
Revision Control
Version N° | Issue Date | Status | Reasons for Change

## Facilities & Shelter
Facilities Maintenance Checklist
Site Name:
Work order: |  | Pending Tasks:
Last Intervention Date:
Intervention Date:
Aproved by:
Performed by:
Item Name | Condition Assesment | Service (If required) | Used Material | Approved Condition
Environmental alarms | Check whether power supply alarms, fire alarms, or smoke alarms are reported. | Notify Field Management about any malfunction. Perform emergency actions if it’s required. In the case of sensors reporting false alarms, replace sensors. | insert used material
Humidity in the shelter | The hygrometer should indicate an humidity range from 5% to 85%. Check for presence of water within the shelter and look for the origin of the leak. | Seal the leaks with the authorized methods | insert used material
Illumination in the shelter | Check whether the routine and emergency illumination in the equipment room is normal. | Look if fuse or light breakers are switched on, change fuses or ligts if its required. | insert used material
Air conditioner | Check whether the air conditioner is working normally.The thermometer indicates a temperature range of 20°C to +50°C | Perform Maintenance procedures as are indicated by the Air conditioner vendor such as: .-Clean the air conditioner’s coils. .-Remove debris from the unit. | insert used material
Protective devices | .-Check whether foam extinguisher or dry powder fire extinguisher is installed in the equipment room. .-Check the pressure and validity period of the extinguisher meets the requirements | Replace or fill the extinguisher | insert used material
Tower Inspection | Check overall condition of Tower .-The foundations and structural supports are solid. .-In the case of a guyed tower, the cables are well secured .-In the case of monopoles, the post is not inclined. .-The ladders are solid and there is no presence of oxidation. .-The paint is well preserved | Notify, Field Management about any degradation on the tower. | insert used material
Shelter Cleanliness. | Check whether cabinets, equipment housing, equipment interior, tables, floor, doors, and windows are clean. There is no damage to the equipment by rats or insects. | All the items to be checked are clean. | insert used material
Additional Actions Required :
Engineer's Signature: |  | Management Sign:
Aproved
Aproved
Aproved
Aproved
Aproved
Aproved
Aproved

## Power System
Power System Maintenance Checklist
Site Name:
Work order: |  | Pending Tasks:
Last Intervention Date:
Intervention Date:
Aproved by:
Performed by:
Item Name | Condition Assesment | Service (If required) | Used Material | Approved Condition
Power cables | Check the connections of power cables carefully. Check wether the power cables are not aging, and there is no corrosion on the connection points. | Notify to the NOC/Field Management if possible to renew cable connections | insert used material
Voltage of Power Distribution Units or Power Supply | Measure the voltage delivered by the Power Distribution Units using a multimeter.The Voltage levels are within the operative ranges. | Notify to the NOC/Field Management if Voltage is out of allowed ranges. | insert used material
GND Cables | Check whether the GND cable and grounding bar are connected properly and the connection points are solid with no corrosion on them | Notify to the NOC/Field Management if possible to renew cable connections | insert used material
Earth resistance | Measure the earth resistance by using an electric earth resistance tester. The grounding resistance of the cabinet is less than 5 ohms. | Notify NOC/Field Management to renew cable connectors or cabling if possible | insert used material
Batteries | Check if battery capacity is within the normal range and the batteries are correctly connected without the presence of corrosion or leaks | Clean Battery Connectors | insert used material
Additional Actions Required :
Engineer's Signature: |  | Management Sign:
Aproved
Aproved
Aproved
Aproved
Aproved

## Baseband&Transmission
Baseband & Transmission Maintenance Checklist
Site Name:
Work order: |  | Pending Tasks:
Last Intervention Date:
Intervention Date:
Aproved by:
Performed by:
Item Name | Condition Assesment | Service (If required) | Used Material | Approved Condition
Fans in Baseband, Transmission equipment and/or cabinet | Check whether the fans are operational.The fans work properly without exceptional sounds generated by friction between the blades of the fan and the sub-rack. | Notify NOC and/or Field Management about any malfunction, replace FAN if it is indicated by NOC / Field Management following the vendor documentation. | insert used material
Cabinet air filter | Check for excessive presence of dust on the air filter | Clean the air filter. | insert used material
Cabinet Exterior. | Check whether there are dents, cracks, holes, or corrosion on the surface of the cabinet. | Seal and paint the cabinet if vendor maintenance documentation allows it. | insert used material
Lock and door of the cabinet. | Check whether the lock is normal. Look for possible obstructions, rust or broken hinges, broken seals | Perform the maintenance as indicated in vendor documentation. | insert used material
Cleanness of the cabinet | Check whether the cabinet is clean. | Clean the Cabinet | insert used material
Fan box | Check the surface and interior of the fan box | Clean the fan box. | insert used material
LEDs on the boards. | Check whether the LEDs on the boards are normal. | Notify to the NOC the presence of the alarm. Schedule corrective actions as required. | insert used material
Additional Actions Required :
Engineer's Signature: |  | Management Sign:
Aproved
Aproved
Aproved
Aproved
Aproved
Aproved
Aproved

## Antenna System
Antenna System Maintenance Checklist
Site Name:
Work order: |  | Pending Tasks:
Last Intervention Date:
Intervention Date:
Aproved by:
Performed by:
Item Name | Condition Assesment | Service (If required) | Used Material | Approved Condition
Radio Units unused RF ports | Check whether the seals are damaged or loose | Replace or tighten the RRU RF Port Caps. | insert used material
Radio Units used RF ports | Check the insulation tape in the antenna and the radio ports. | Replace the seals or insulation tape. | insert used material
Radio Unit Fiber and Power | Check the Isolation to the Power Port and Fibers | Replace the insulating rubber or tape. | insert used material
Radio unit and Antenna Mounting | Check whether there are loose screws in the Radio Unit and Antenna Mounting Kit | Tight the screws at the right torque. | insert used material
Antenna Mechanical Tilt and Azimuth | Check whether the Antenna Mechanical Tilt and Azimuth match with the corresponding values in the Site Documentation | Adjust the Mechanical Tilt and Azimuth following the maintenance guidelines of the Antenna Vendor. | insert used material
Microwave Dish Connections | Check the isolation of Intermediate Frequency cable or Ethernet cable and power cable as appropriate. | Replace the seals or insulation tape. | insert used material
Microwave Dish Mounting | Check the fixing screws of the mounting kit are tight with the right torque | Tight the screws at the right torque, Replace the seals or insulation tape. | insert used material
Additional Actions Required :
Engineer's Signature: |  | Management Signature:
Aproved
Aproved
Aproved
Aproved
Aproved
Aproved
Aproved